## Introduction
Space Heating Boiler-Furnace Tune-Up
Introduction
The Space Heating Boiler-Furnace Tune-Up Application and Savings Tool calculates estimated energy savings and incentive amounts in accordance with the Energy Management Program guidelines and the savings protocols agreed to by the utility working group. The form is designed to provide the necessary information and data collection needed to participate in the program.
Instructions
1. Combustion testing for each piece of equipment must be performed at a mid-range firing rate representative of average building operating conditions over the course of the heating season. Firing rate should be consistent for pre- and post tune-up. 2. Beginning with the "Application" tab, input the project data into all light blue shaded fields. Some input cells contain drop down menus with a list of entry choices for that particular field. 3. Fill out the appropriate "Tune-Up Checklist" tab by entering equipment on a separate line for each unit and confirm the tune-up activities completed. The equipment location, unit ID and building type will pre-fill in the related "Equipment Details" tab. 4. In the appropriate "Equipment Details" tab, enter the technical information for each unit. All light blue shaded fields are required, grey fields calculate automatically. 5. Read the "Terms and Conditions" tab, acknowledged in the "Project Closeout" tab. 6. Print the Project Closeout Form, which populates automatically based on the "Equipment Details" tab. Both Customer and Contractor must sign form. 7. Email this completed application workbook, signed scope of work / rebate request, itemized invoice (labor / material), combustion test pre- and post results, and payee W9 to the program as indicated under the "Project Closeout" tab. | move instructions here
Project Eligibility
Minimum Eligibility Requirements
To participate, the customer must have an active commercial natural gas account in good standing. Eligible units must not be included under a standing maintenance contract and must not have had a tune-up in the last three years. This application covers tune-ups for space heating equipment only. Other equipment (process or other use) is ineligible.
Eligible Equipment
Boilers - space heating Furnaces - space heating
Incentives
Boiler Tune-up - $1.00 per Mbtu Input Capacity Furnace Tune-up - $150 per furnace Incentives are capped at 100% of the tune-up cost, applied at the unit level.

## Application
Space Heating Boiler-Furnace Tune-Up Application |  |  |  |  | version 2.00
General Project Information
| Company Name: |  |  | Facility Street Address:
| Customer Name / Title: |  |  | Facility City / Zip Code:
| Customer Contact Phone: |  |  | Facility Type:
| Customer Contact Email: |  |  | Gas Account Number:
Contractor Information
| Company Name: |  |  | Contractor Address:
| Contractor Phone: |  |  | City / Zip Code:
Contractor Email:
Additional Information
|  | Project in Urban Enterprise Zone?: | To determine if project is in Urban Enterprise or Opportunity Zone:
|  | Project in Opportunity Zone?: | Visit website below and enter address in search box
|  | K-12 School?: | https://www.arcgis.com/apps/webappviewer/index.html?id=96ec274c50a34890b23263f101e4ad9b
|  | Municipality or County?: | At left check Urban Enterprise or Opportunity Zone if applicable

## Tune-Up Checklist-Boiler
Space Heating Boiler Tune-Up Checklist
[5 empty] | Tune-up activities eligible to be performed by tune-up technician | [14 empty] | Tune-up activies eligible to be performed by internal maintenance staff or tune-up technician at periods of boiler shutdown
[5 empty] | Select "Yes" or "No" in columns F through T for each item completed by tune-up technician | [14 empty] | Select "Yes" or "No" in columns U through AC for each item completed by in-house maintenance staff or tune-up technician
| Boiler Location (Facility or Building Name) | Boiler Unit ID(s) | Building Type (select from dropdown) | Years since last Boiler tune-up | Measure combustion efficiency using an electronic flue gas analyzer | Check for proper venting | Complete visual inspection of system piping and insulation | Check safety controls | Check adequacy of combustion air intake | Perform all flame safeguard and safety trip checks | Check all hand hole plates and manhole plates for leaks at normal operating temperatures and pressures | Adjust airflow and reduce excessive stack temperatures | Adjust burner and gas input, manual or motorized draft control | Check pilot electrode and adjust or replace | Make necessary adjustments to burner for proper combustion | Clean fireside surfaces | Cleanburner and burner pilot | Clean air damper and blower assembly | Troubleshoot any boiler system problems as requested by on-site personnel | Inspect all refractory. Patch and wash coast as required | Inspect gaskets on front and rear doors and replace as necessary | Seal and close front and rear doors properly | Clean low and auxiliary low water cut-off controls, then re-9nstall using new gaskets | Clean plugs in control piping | Remove all hand hole and manhole plates. Flush boiler with water to remove loose scale and sediment | Replace all hand hole and manhole plates with new gaskets | Open feedwater tank manway, inspect and clean as required. Replace manway plate with new gasket | Clean motor starter contacts and check operation
Example | Main Building | EX-1 | Office - Large | 3 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## Tune-Up Checklist-Furnace
Space Heating Furnace Tune-Up Checklist
Tune-up activities eligible to be performed by tune-up technician
Select "Yes" or "No" in columns F through T for each item completed by tune-up technician
| Furnace Location (Facility or Building Name) | Furnace Unit ID(s) | Building Type (select from dropdown) | Years since last Furnace tune-up | Measure combustion efficiency using an electronic flue gas analyzer | Check and clean blower assembly and components per manufacturer's recommendations | Check ignition system and safety systems and clean and adjust as needed | Check and clean heat exchanger per manufacturer's recommendations | Check air filter and clean or replace per manufacturer's recommendations | Check for correct line and load volts/amps | Check thermostat operation is per manufacturer's recommendations | Inspect for gas leaks | Inspect exhaust/flue for proper attachment and operation | Inspect control box, wiring and controls for proper connections and performance | Inspect duct work connected to furnace for leaks or blockages | Measure temperature rise and adjust flow as needed | Where applicable lubricate motor and inspect and replace fan belt if required | Clean burner per manufacturer's recommendations and adjust as needed | Perform carbon monoxide test and adjust heating system until results are within standard industry acceptable limits
Example | Main Building | EX-1 | Retail – Small | 3 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## Equipment Details-Boiler
Space Heating Boiler Tune-Up Details
Number of Eligible Units | Total Annual Savings Therms | Total Rebate | Scope Project Cost
0 | 0 | 0 | 0
| Boiler Location | Boiler Unit ID(s) | Building Type | Boiler Manufacturer | Boiler Model Number | Boiler Input Capacity (BTUs/Hr) | # of Units | Age of Existing Equipment (Years) | Eligibility Status | Effbefore - Efficiency before based on testing | Effafter - Efficiency before based on testing | Include in Scope? | Eligible | Tune-Up Cost | Notes | Ei - Boiler tune-up Efficiency improvement | Default Annual Heating EFLH | Annual Therm Savings / Unit | Total Therm Savings If Eligible | Estimated Incentive / Unit | Estimated Total Boiler Incentive (capped at cost) | Tune-up Cost for those in Scope | Eligible Units
Example | Main Building | EX-1 | Office - Large | Clever Brooks | CBLE-4D | 2092000 | 1 | 5 | No Prior Tune-up Application | 77% | 81.5% | Yes | Yes | 2000 |  | 4.5% | 2034 | 2486.7631 | 2486.7631 | 2092 | 2000 | 2000 | 1
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
Total | [13 empty] | 0 |  |  |  | 0 | 0 |  | 0 | 0 | 0

## Equipment Details-Furnace
Space Heating Furnace Tune-Up Details
Number of Eligible Units | Total Annual Savings Therms | Total Rebate | Scope Project Cost
0 | 0 | 0 | 0
* * * * | Furnace Location | Furnace Unit ID(s) | Building Type | Furnace Manufacturer | Furnace Model Number | Furnace Input Capacity (BTUs/Hr) | # of Units | Age of Existing Equipment (Years) | Eligibility Status | Effbefore - Efficiency before based on testing | Effafter - Efficiency before based on testing | Include in Scope? | Eligible | Tune-Up Cost | Notes | Ei - Boiler tune-up Efficiency improvement | Default Annual Heating EFLH | Annual Therm Savings / Unit | Total Therm Savings If Eligible | Estimated Incentive / Unit | Estimated Total Furnace Incentive (capped at cost) | Tune-up Cost for those in Scope | Eligible Units
Example | Main Building | EX-1 | Retail – Small | Comfortmaker | N95ESN1202422A | 300000 | 1 | 5 | Furnace Age < 1 Year | 81.5% | 83% | Yes | No | 300 |  | 1.5% | 545 | 30.092 | 0 | 0 | 0 | 300 | 0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
Total | [13 empty] | 0 |  |  |  | 0 | 0 |  | 0 | 0 | 0

## Project Closeout-Boiler
1
1 | Space Heating Boiler Tune-Up
1 | Project Closeout
1
1
1 |  | Participating Customer:
1 |  | Participating Contractor:
1 |  | Facility Address: | [5 empty] | NJ
1 |  |  | Street |  |  |  | City | State | Zip
1
1
1 | When the tune-up is complete, verify the Scope of Work fields below. Submit the signed Closeout form with the required documents listed below to the program via email to:
SJGBusiness@appliedenergygroup.com
1 | Required Documents:
| □ | Boiler - Furnace Tune-Up Application (this excel workbook)
| □ | Signed Project Closeout document (print, sign and scan this form)
| □ | Final invoice for tune-up listing itemized equipment and labor costs
| □ | W9 Form for payee
Scope of Work
The work performed by the Participating Contractor in connection with the Project is outlined below:
Estimated Rebate
| Measure Description |  |  | Unit Quantity | Project Cost |  |  | Amount
| Boiler Tune-up |  |  | 0 | 0 |  |  | 0
1
1 | By signing below, the Customer and Contractor agree the Scope of Work above was completed. Customer certifies they have the authority to contract for work in the Facility in connection with the Measures listed and, if the Customer does not own the Facility, the Owner has granted permission to Customer for performance of such work. Customer acknowledges and agrees to the Terms and Conditions contained within this workbook.
1
1
1
1
1 | Participating Customer |  |  | Date |  | Participating Contractor |  |  |  | Date

## Project Closeout-Furnace
1
1 | Space Heating Furnace Tune-Up
1 | Project Closeout
1
1
1 |  | Participating Customer:
1 |  | Participating Contractor:
1 |  | Facility Address: | [5 empty] | NJ
1 |  |  | Street |  |  |  | City | State | Zip
1
1
1 | When the tune-up is complete, verify the Scope of Work fields below. Submit the signed Scope of Work with the required documents listed below to the program via email to:
SJGBusiness@appliedenergygroup.com
1 | Required Documents:
| □ | Boiler - Furnace Tune-Up Application (this excel workbook)
| □ | Signed Project Closeout document (print, sign and scan this form)
| □ | Final invoice for tune-up listing itemized equipment and labor costs
| □ | W9 Form for payee
Scope of Work
The work performed by the Participating Contractor in connection with the Project is outlined below:
Estimated Rebate
| Measure Description |  |  | Unit Quantity | Project Cost |  |  | Amount
| Furnace Tune-up |  |  | 0 | 0 |  |  | 0
1
1 | By signing below, the Customer and Contractor agree the Scope of Work above was completed. Customer certifies they have the authority to contract for work in the Facility in connection with the Measures listed and, if the Customer does not own the Facility, the Owner has granted permission to Customer for performance of such work. Customer acknowledges and agrees to the Terms and Conditions contained within this workbook.
1
1
1
1
1 | Participating Customer |  |  | Date |  | Participating Contractor |  |  |  | Date

## Lookups (hidden)
Yes / No | Building Type | EFLH Cooling | EFLH Heating
| Auto Repair | 426 | 1910
Yes | Education – Primary School | 394 | 840
No | Education – Secondary School | 466 | 901
| Education – Community College | 846 | 1431
| Education – University | 1208 | 1191
| Grocery | 1279 | 191
| Medical – Hospital | 1424 | 3366
| Medical – Clinic | 736 | 681
| Lodging Hotel (Guest Rooms) | 2918 | 1077
| Lodging Motel | 1233 | 619
| Manufacturing – Light Industrial | 549 | 714
| Office - Large | 720 | 2034
| Office - Small | 955 | 431
| Public Assembly/Meeting Hall | 669 | 603
| Restaurant – Sit-Down | 574 | 821
| Restaurant – Fast-Food | 645 | 813
| Retail – 3-Story Large | 1068 | 2101
| Retail – Single-Story Large | 1068 | 2101
| Retail – Small | 882 | 545
| Religious Worship | 279 | 722
| Storage Conditioned | 400 | 452
| Storage Unconditioned | 400 | 452
| Warehouse | 400 | 452
| Other | 736 | 681

## Development (hidden)
Revision History
Current Version #: | 2
Current Effective Date: | 2023-06-29
Date | Changes | Version Number | Initials
2022-04-28 | Created SJI Tune-up Workbook from ACE Tune-up Version. Small Business Furnace Tune-Up (removed electric savings) and Space Heating Boiler Tune-Up measures. The measures are referenced from Illinois TRM v. 9.0 Vol.2 and in Reference tab. | 1 | KAB
2022-07-07 | Corrected SJG to ETG in T&Cs (Pre- and Post-Inspection section | 1.01 | KAB
2023-06-29 | Corrected dropdowns for eligibility, added eligibility column, corrected logos on close-out tabs, corrected savings and incentive calculations based on eligibility | 2 | KAB